## Setup
Notes
Settings
Spreadsheet Version | 0.4.2 |  |  | Do NOT change this unless advised
User Id | name |  |  | This is the tag that is applied to your running instances so that you can identify which instances are yours.
OpenStudio Server Version | 1.14.4 |  |  | Choose which OpenStudio Server Version to Use. Do NOT change this unless advised. Note that this is not the OpenStudio version. See mappings here: http://developer.nrel.gov/downloads/buildings/openstudio/rsrc/amis_v2.json
Cluster Name | default |  |  | This is the name used to identify the compute cluster (snake-cased). If you use this name in other spreadsheets, then you are able to submit multiple jobs to the same compute cluster.
Server Instance Type | m3.xlarge | 4 Cores - Recommended for Server | $0.28/hour | Use a minimum of 2 cores for server.
Worker Instance Type | c3.8xlarge | 16 Cores - Worker Only - Recommended for Worker | $1.68/hour | Depends on how many simuations. If you are testing, then you can select a smaller instance.
Worker Nodes | 1 |  |  | Number of worker nodes to start.
Running Setup
Analysis Name | SEB4 baseboard PSO 2013 |  |  | Display name of the analysis
Measure Directory | ../Calibration_example/measures |  |  | Relative to this spreadsheet or absolute path
Export Directory | ../analysis |  |  | Relative to this spreadsheet or absolute path
Allow Multiple Jobs | TRUE |  |  | Do NOT change this unless advised
Use Server As Worker | TRUE |  |  | Enable this for certain analysis. Typically do not use the server as a worker.
Simulate Data Point Filename | simulate_data_point.rb |  |  | Do NOT change this unless advised
Run Data Point Filename | run_openstudio_workflow_monthly.rb |  |  | Do NOT change this unless advised
Problem Definition | Problem Type |  |  | Place any Problem Specific entries here. The names will be downcased and underscored automatically, so either enter them as readable or already "snake_cased". Note the values won't be downcased or snake_cased.
Analysis Type | pso
Algorithm Setup | Configuration Values | Allowed Values and Description | Override Defaults (Enter values here to override the Defaults in Column B) | Place any Problem Specific entries here. The names will be downcased and underscored automatically, so either enter them as readable or already "snake_cased". Note the values won't be downcased or snake_cased.
npart | 94
maxit | 7
maxfn | 3000
lambda | 0.9
c2 | 1
c1 | 1
boundary | reflecting
topology | random
xini | lhs
vini | lhs2011
abstol | 0.01
reltol | 0.01
method | spso2011
Weather Files | Path (relative to this spreadsheet or absolute path) | Weather files in the .zip format. Can list individually or use a wild card
Weather File | ../Calibration_example/weather/SRRL_2013AMY_60min.epw
Models | Identifier | File Type | Path (relative to this spreadsheet or absolute path) | If there are more than one seed models, then you will submit the same analysis for each seed model.
Model |  | OSM | ../Calibration_example/seeds/SEB4_baseboard.osm
Other Library Files | Directory to Unpack to | Files to include (relative to this spreadsheet or absolute path). If a directory then it will include all subfolders and files |  | If extra library files are needed then include them here. These are typically preprocessors or postprocessors and require custom measures to use.
Directory | calibration_data | ../Calibration_example/lib

## Variables
|  |  | Inputs | [6 empty] | Continuous Variable Description |  |  |  |  | Discrete Variable Description |  |  |  |  | Other Notes
# Measure Enabled | Measure Display Name | Measure Directory Name | Measure Class Name
# Variable | type | Measure Directory | Parameter Display Name (will make machine name) | Parameter Name in Measure | Parameter Short Display Name | Variable Type | Units | Static/Default Value | Enumerations | Min | Max | Mean | Std Dev | Delta X | Discrete Values | Discrete Weights | Distribution | Data Source | Notes | Typical var to eui relationship | Screening Min | Screening Max | Screening Mean | Screening Std Dev
TRUE | AddMonthlyJSONUtilityDataElectric | AddMonthlyJSONUtilityData | AddMonthlyJSONUtilityData | RubyMeasure
| argument |  | Path to JSON | json |  | string |  | ../../../lib/calibration_data/electric.json
| argument |  | Variable Name | variable_name |  | string |  | Electric Bill
| argument |  | Fuel Type | fuel_type |  | string |  | Electricity
| argument |  | Consumption Unit | consumption_unit |  | string |  | kWh
| argument |  | data key name | data_key_name |  | string |  | tot_kwh
| argument |  | Start date | start_date |  | string |  | 2013-01-1
| argument |  | End date | end_date |  | string |  | 2013-12-31
| argument |  | remove existing Utility Bill data | remove_existing_data |  | Bool |  | TRUE
| argument |  | Set RunPeriod | set_runperiod |  | Bool |  | TRUE
TRUE | AddMonthlyJSONUtilityDataGas | AddMonthlyJSONUtilityData | AddMonthlyJSONUtilityData | RubyMeasure
| argument |  | Path to JSON | json |  | string |  | ../../../lib/calibration_data/gas.json
| argument |  | Variable Name | variable_name |  | string |  | Gas Bill
| argument |  | Fuel Type | fuel_type |  | string |  | Gas
| argument |  | Consumption Unit | consumption_unit |  | string |  | therms
| argument |  | data key name | data_key_name |  | string |  | tot_therms
| argument |  | Start date | start_date |  | string |  | 2013-01-1
| argument |  | End date | end_date |  | string |  | 2013-12-31
| argument |  | remove existing Utility Bill data | remove_existing_data |  | Bool |  | FALSE
TRUE | Calibration Reports Enhanced | CalibrationReportsEnhanced | CalibrationReportsEnhanced | ReportingMeasure
TRUE | ReduceSpaceInfiltrationByPercentage | ReduceSpaceInfiltrationByPercentage | ReduceSpaceInfiltrationByPercentage | RubyMeasure
| argument |  | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type |  | Choice |  | *Entire Building* | ¦*Entire Building*¦
| variable |  | Space Infiltration Reduction | space_infiltration_reduction_percent |  | Double |  | 0 |  | 0 | 100 | 15 | 16.6667 | 1 |  |  | uniform
| argument |  | Constant Coefficient | constant_coefficient |  | Double |  | 1
| argument |  | Temperature Coefficient | temperature_coefficient |  | Double |  | 0 |  | 0 | 0.1 | 0.05 | 0.016667 | 0.01 |  |  | uniform
| argument |  | Wind Speed Coefficient | wind_speed_coefficient |  | Double |  | 0
| argument |  | Wind Speed Squared Coefficient | wind_speed_squared_coefficient |  | Double |  | 0
| argument |  | Increase in Material and Installation Costs for Building per Affected Floor Area ($/ft^2). | material_and_installation_cost |  | Double |  | 0
| argument |  | O & M Costs for Construction per Affected Floor Area ($/ft^2). | om_cost |  | Double |  | 0
| argument |  | O & M Frequency (whole years). | om_frequency |  | Integer |  | 1
TRUE | Reduce Lighting Loads by Percentage | ReduceLightingLoadsByPercentage | ReduceLightingLoadsByPercentage | RubyMeasure
| argument |  | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type |  | Choice |  | *Entire Building* | ¦*Entire Building*¦
| argument |  | Lighting Power Reduction | lighting_power_reduction_percent |  | Double |  | 0 |  | -40 | 40 | 0 | 13.3333 | 1 |  |  | uniform
| argument |  | Increase in Material and Installation Cost for Lighting per Floor Area (%). | material_and_installation_cost |  | Double |  | 0
| argument |  | Increase in Demolition Costs for Lighting per Floor Area (%). | demolition_cost |  | Double |  | 0
| argument |  | Years Until Costs Start (whole years). | years_until_costs_start |  | Integer |  | 0
| argument |  | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const |  | Bool |  | TRUE
| argument |  | Expected Life (whole years). | expected_life |  | Integer |  | 15
| argument |  | Increase O & M Costs for Lighting per Floor Area (%). | om_cost |  | Double |  | 0
| argument |  | O & M Frequency (whole years). | om_frequency |  | Integer |  | 1
TRUE | Reduce Electric Equipment Loads by Percentage | ReduceElectricEquipmentLoadsByPercentage | ReduceElectricEquipmentLoadsByPercentage | RubyMeasure
| argument |  | Apply the Measure to a Specific Space Type or to the Entire Model | space_type |  | Choice |  | *Entire Building* | ¦*Entire Building*¦
| variable |  | Electric Equipment Power Reduction | elecequip_power_reduction_percent |  | Double | % | 0 |  | -80 | 80 | 0 | 26.6667 | 1 |  |  | uniform
| argument |  | Increase in Material and Installation Cost for Electric Equipment per Floor Area | material_and_installation_cost |  | Double | % | 0
| argument |  | Increase in Demolition Costs for Electric Equipment per Floor Area | demolition_cost |  | Double | % | 0
| argument |  | Years Until Costs Start | years_until_costs_start |  | Integer | whole years | 0
| argument |  | Demolition Costs Occur During Initial Construction | demo_cost_initial_const |  | Bool |  | FALSE
| argument |  | Expected Life | expected_life |  | Integer | whole years | 15
| argument |  | Increase O & M Costs for Electric Equipment per Floor Area | om_cost |  | Double | % | 0
| argument |  | O & M Frequency | om_frequency |  | Integer | whole years | 1
TRUE | Set Gas Burner Efficiency | SetGasBurnerEfficiency | SetGasBurnerEfficiency | RubyMeasure
| argument |  | Choose an Air Loop with a two speed DX Cooling Unit to Alter. | object |  | Choice |  | *All Air Loops* | ¦*All Air Loops*¦
| variable |  | Burner Efficiency (fractional) | eff |  | Double | % | 0.8 |  | 0.78 | 0.98 | 0.8 | 0.033333 | 1 |  |  | uniform
| argument |  | Remove Baseline Costs From Effected Cooling Coil DX Two Speed Units? | remove_costs |  | Bool |  | FALSE
| argument |  | Increase in Material and Installation Cost for Electric Equipment per Floor Area | material_cost |  | Double | % | 0
| argument |  | Increase in Demolition Costs for Electric Equipment per Floor Area | demolition_cost |  | Double | % | 0
| argument |  | Years Until Costs Start | years_until_costs_start |  | Integer | whole years | 0
| argument |  | Demolition Costs Occur During Initial Construction | demo_cost_initial_const |  | Bool |  | FALSE
| argument |  | Expected Life | expected_life |  | Integer | whole years | 15
| argument |  | Increase O & M Costs for Electric Equipment per Floor Area | om_cost |  | Double | % | 0
| argument |  | O & M Frequency | om_frequency |  | Integer | whole years | 1
TRUE | Set COP for Single Speed DX Cooling Units | SetCOPforSingleSpeedDXCoolingUnits | SetCOPforSingleSpeedDXCoolingUnits | RubyMeasure
| argument |  | Choose an Air Loop with a single speed DX Cooling Unit to Alter. | object |  | Choice |  | *All Air Loops* | ¦*All Air Loops*¦
| variable |  | Rated COP | cop |  | Double | % | 4 |  | 2 | 5 | 4 | 0.5 | 0.25 |  |  | uniform
| argument |  | Remove Baseline Costs From Effected Cooling Coil DX Two Speed Units? | remove_costs |  | Bool |  | FALSE
| argument |  | Increase in Material and Installation Cost for Electric Equipment per Floor Area | material_cost |  | Double | % | 0
| argument |  | Increase in Demolition Costs for Electric Equipment per Floor Area | demolition_cost |  | Double | % | 0
| argument |  | Years Until Costs Start | years_until_costs_start |  | Integer | whole years | 0
| argument |  | Demolition Costs Occur During Initial Construction | demo_cost_initial_const |  | Bool |  | FALSE
| argument |  | Expected Life | expected_life |  | Integer | whole years | 15
| argument |  | Increase O & M Costs for Electric Equipment per Floor Area | om_cost |  | Double | % | 0
| argument |  | O & M Frequency | om_frequency |  | Integer | whole years | 1
TRUE | Improve Fan Belt Efficiency | ImproveFanBeltEfficiency | ImproveFanBeltEfficiency | RubyMeasure
| argument |  | Choose an Air Loop to Alter. | object |  | Choice |  | *All Air Loops* | ¦*All Air Loops*¦
| variable |  | Motor Efficiency Change(%). | motor_eff |  | Double | % | 0 |  | -20 | 14 | 0 | 5.6667 | 1 |  |  | uniform
| variable |  | Fan Efficiency Change(%). | fan_eff |  | Double | % | 0 |  | -20 | 30 | 0 | 8.3333 | 1 |  |  | uniform
| argument |  | Remove Baseline Costs From Effected Cooling Coil DX Two Speed Units? | remove_costs |  | Bool |  | FALSE
| argument |  | Increase in Material and Installation Cost for Electric Equipment per Floor Area | material_cost |  | Double | % | 0
| argument |  | Increase in Demolition Costs for Electric Equipment per Floor Area | demolition_cost |  | Double | % | 0
| argument |  | Years Until Costs Start | years_until_costs_start |  | Integer | whole years | 0
| argument |  | Demolition Costs Occur During Initial Construction | demo_cost_initial_const |  | Bool |  | FALSE
| argument |  | Expected Life | expected_life |  | Integer | whole years | 15
| argument |  | Increase O & M Costs for Electric Equipment per Floor Area | om_cost |  | Double | % | 0
| argument |  | O & M Frequency | om_frequency |  | Integer | whole years | 1
TRUE | Adjust Thermostat Setpoints by Degrees | AdjustThermostatSetpointsByDegrees | AdjustThermostatSetpointsByDegrees | RubyMeasure
| variable |  | Degrees Fahrenheit to Adjust Cooling Setpoint By | cooling_adjustment |  | Double | deg F | 0 |  | -6 | 2 | 0 | 1.3333 | 1 |  |  | uniform
| variable |  | Degrees Fahrenheit to Adjust heating Setpoint By | heating_adjustment |  | Double | deg F | 0 |  | -5 | 3.9 | 0 | 1.4833 | 1 |  |  | uniform
| argument |  | Alter Design Day Thermostats | alter_design_days |  | Bool |  | FALSE
TRUE | Change Exterior Wall Thermal Properties | ChangeExteriorWallThermalProperties | ChangeExteriorWallThermalProperties | RubyMeasure
| variable |  | Wall total R-value multiplier | r_value_mult |  | Double |  | 1 |  | 0.5 | 4 | 1.75 | 0.25 | 0.1 |  |  | uniform
| variable |  | Exterior wall solar absorptance multiplier | solar_abs_mult |  | Double |  | 1 |  | 0.1 | 3 | 1.75 | 0.25 | 0.1 |  |  | uniform
| variable |  | Exterior wall thermal mass multiplier | thermal_mass_mult |  | Double |  | 1 |  | 0.5 | 3 | 1.75 | 0.25 | 0.1 |  |  | uniform
TRUE | Change Roof Thermal Properties | ChangeRoofThermalProperties | ChangeRoofThermalProperties | RubyMeasure
| variable |  | Roof total R-value multiplier | r_value_mult |  | Double |  | 1 |  | 0.5 | 3 | 1.75 | 0.25 | 0.1 |  |  | uniform
| variable |  | Roof solar absorptance multiplier | solar_abs_mult |  | Double |  | 1 |  | 0.5 | 4 | 1.75 | 0.25 | 0.1 |  |  | uniform
| variable |  | Roof thermal mass multiplier | thermal_mass_mult |  | Double |  | 1 |  | 0.5 | 3 | 1.75 | 0.25 | 0.1 |  |  | uniform
TRUE | Change Electric Baseboard | ChangeElectricBaseboard | ChangeElectricBaseboard | RubyMeasure
| argument |  | Baseboard Efficiency % | base_eff |  | Double | % | 1 |  | 0.9 | 1 | 0.95 | 0.016667 | 0.1 |  |  | uniform
| variable |  | Baseboard Nominal Capacity (W) | nom_cap |  | Double | % | 1450 |  | 0 | 3000 | 1450 | 500 | 10 |  |  | uniform
TRUE | Server Directory Cleanup | ServerDirectoryCleanup | ServerDirectoryCleanup | ReportingMeasure

## Outputs
Outputs
Variable Display Name | Short Display Name | Taxonomy Identifier | Name | Units | Variable Type | Visualize | Export | Objective Function | Objective Function Target | Scale | Objective Function Group
Display Name for Reports | Short display names are used for plots and exported to metadata | Machine Name thats Link to Dencity Taxonomy | Measure/Variable Unique Name |  | double, integer, bool | true/false | true/false | true/false | double | double | integer | Temp
Total Site Energy Intensity |  | total_site_energy_intensity | standard_report_legacy.total_energy | MJ/m2 | Double | FALSE | TRUE | FALSE
Total Source Energy Intensity |  | total_source_energy_intensity | standard_report_legacy.total_source_energy | MJ/m2 | Double | FALSE | TRUE | FALSE
Total Natural Gas Intensity | NG EUI | total_natural_gas_intensity | standard_report_legacy.total_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Total Electricity Intensity | Elec EUI | total_electricity_intensity | standard_report_legacy.total_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Natural Gas Heating Intensity |  |  | standard_report_legacy.heating_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Cooling Electricity Intensity |  |  | standard_report_legacy.cooling_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Interior Lighting Electricity Intensity |  |  | standard_report_legacy.interior_lighting_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Exterior Lighting Electricity Intensity |  |  | standard_report_legacy.exterior_lighting_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Equipment Electricity Intensity |  |  | standard_report_legacy.interior_equipment_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Equipment Natural Gas Intensity |  |  | standard_report_legacy.interior_equipment_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Experior Equipment Electricity Intensity |  |  | standard_report_legacy.exterior_equipment_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Fans Electricity Intensity |  |  | standard_report_legacy.fans_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Pumps Electricity Intensity |  |  | standard_report_legacy.pumps_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Heat Rejection Electricity Intensity |  |  | standard_report_legacy.heat_rejection_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Humidification Electricity Intensity |  |  | standard_report_legacy.humidification_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Water Systems Electricity Intensity |  |  | standard_report_legacy.water_systems_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Water Systems Natural Gas Intensity |  |  | standard_report_legacy.water_systems_natural_gas | MJ/m2 | Double | FALSE | TRUE | FALSE
Refrigeration Electricity Intensity |  |  | standard_report_legacy.refrigeration_electricity | MJ/m2 | Double | FALSE | TRUE | FALSE
Unmet Cooling Hours |  |  | standard_report.time_setpoint_not_met_during_occupied_cooling | hrs | Double | FALSE | TRUE | FALSE
Unmet Heating Hours |  |  | standard_report.time_setpoint_not_met_during_occupied_heating | hrs | Double | FALSE | TRUE | FALSE
Total Unmet Hours |  |  | standard_report.time_setpoint_not_met_during_occupied_hours | hrs | Double | FALSE | TRUE | FALSE
Building Area |  |  | standard_report.total_building_area | m2 | Double | FALSE | TRUE | FALSE
Total Electricity Consumption Modeled |  |  | calibration_reports_enhanced.electric_bill_consumption_modeled | kWh | Double | FALSE | TRUE | FALSE
Total Gas Consumption Modeled |  |  | calibration_reports_enhanced.gas_bill_consumption_modeled | therms | Double | FALSE | TRUE | FALSE
Electric RMSE |  |  | calibration_reports_enhanced.electric_bill_rmse | % | Double | FALSE | TRUE | FALSE
Gas RMSE |  |  | calibration_reports_enhanced.gas_bill_rmse | % | Double | FALSE | TRUE | FALSE
Electric CVRMSE |  |  | calibration_reports_enhanced.electric_bill_consumption_cvrmse | % | Double | TRUE | TRUE | TRUE
Electric NMBE |  |  | calibration_reports_enhanced.electric_bill_consumption_nmbe | % | Double | TRUE | TRUE | TRUE
Gas CVRMSE |  |  | calibration_reports_enhanced.gas_bill_consumption_cvrmse | % | Double | TRUE | TRUE | TRUE
Gas NMBE |  |  | calibration_reports_enhanced.gas_bill_consumption_nmbe | % | Double | TRUE | TRUE | TRUE
Electric CVRMSE within limit |  |  | calibration_reports_enhanced.electric_bill_cvrmse_within_limit |  | Double | TRUE | TRUE | FALSE
Electric NMBE within limit |  |  | calibration_reports_enhanced.electric_bill_nmbe_within_limit |  | Double | TRUE | TRUE | FALSE
Gas CVRMSE within limit |  |  | calibration_reports_enhanced.gas_bill_cvrmse_within_limit |  | Double | TRUE | TRUE | FALSE
Gas NMBE within limit |  |  | calibration_reports_enhanced.gas_bill_nmbe_within_limit |  | Double | TRUE | TRUE | FALSE

## BCL Measure Data
FALSE | Add Cost per Area to Construction | AddCostPerAreaToConstruction | RubyMeasure
| argument | Choose a Construction to Add Costs to. | construction | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Area to Unused Construction | AddCostPerAreaToUnusedConstruction | RubyMeasure
| argument | Choose a Construction to Add Costs to. | construction | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Building | AddCostPerFloorAreaToBuilding | RubyMeasure
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Name for Life Cycle Cost Object. | lcc_name | static | String | Building - Life Cycle Costs
| argument | Material and Installation Costs for the Building per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the Builiding per Floor Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Electric Equipment | AddCostPerFloorAreaToElectricEquipment | RubyMeasure
| argument | Choose a Watts per Area Electric Equipment Definition to Add Costs to. | equip_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Lights | AddCostPerFloorAreaToLights | RubyMeasure
| argument | Choose a Watt per Area Lights Definition to Add Costs to. | lights_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost per Floor Area to Unused Lights | AddCostPerFloorAreaToUnusedLights | RubyMeasure
| argument | Choose a Watt per Area Lights Definition to Add Costs to. | lights_def | static | Choice
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Definition per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Definition per Floor Area ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Definition per Floor Area ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Cost To Supply Side HVAC Component by Air Loop | AddCostToSupplySideHVACComponentByAirLoop | RubyMeasure
| argument | Select an HVAC Air Loop Supply Side Component Type. | hvac_comp_type | static | Choice
| argument | Choose an Air Loop to Add Costs to. | object | static | Choice | **All Air Loops** | ¦**All Air Loops**¦
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs per Component ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Component ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Component ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Daylight Sensor at Center of Spaces with a Specified Space Type Assigned | AddDaylightSensors | RubyMeasure
| argument | Add Daylight Sensors to Spaces of This Space Type | space_type | static | Choice
| argument | Daylighting Setpoint (fc) | setpoint | static | Double | 45
| argument | Daylighting Control Type | control_type | static | Choice | Continuous/Off | ¦None,Continuous,Stepped,Continuous/Off¦
| argument | Daylighting Minimum Input Power Fraction(min = 0 max = 0.6) | min_power_fraction | static | Double | 0.3
| argument | Daylighting Minimum Light Output Fraction (min = 0 max = 0.6) | min_light_fraction | static | Double | 0.2
| argument | Sensor Height (inches) | height | static | Double | 30
| argument | Material and Installation Costs per Space for Daylight Sensor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Space for Daylight Sensor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Space for Daylight Sensor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Exterior Lights | AddExteriorLights | RubyMeasure
| argument | Exterior Lighting Design Power (W) | ext_lighting_level | static | Double | 1000
| argument | End-Use SubCategory | end_use_subcategory | static | String | Exterior Facade Lighting
| argument | Remove Existing Exterior Lights in the Project? | remove_existing_ext_lights | static | Bool | FALSE
| argument | Material and Installation Costs for Exterior Lights ($). | material_cost | static | Double | 0
| argument | Demolition Costs for Exterior Lights ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Exterior Lights ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Add Output Diagnostics | AddOutputDiagnostics | EnergyPlusMeasure
| argument | Ouput Diagnostic Value. | outputDiagnostic | static | Choice | DisplayExtraWarnings | ¦DisplayAllWarnings,DisplayExtraWarnings,DisplayUnusedSchedules,DisplayUnusedObjects,DisplayAdvancedReportVariables,DisplayZoneAirHeatBalanceOffBalance,DoNotMirrorDetachedShading,DisplayWeatherMissingDataWarnings,ReportDuringWarmup,ReportDetailedWarmupConvergence¦
FALSE | Add Output Variable | AddOutputVariable | RubyMeasure
| argument | Enter Variable Name. | variable_name | static | String
| argument | Reporting Frequency. | reporting_frequency | static | Choice | hourly | ¦detailed,timestep,hourly,daily,monthly¦
FALSE | Add Overhangs by Projection Factor | AddOverhangsByProjectionFactor | RubyMeasure
| argument | Projection Factor (overhang depth / window height) | projection_factor | static | Double | 0.5
| argument | Cardinal Direction | facade | static | Choice | South | ¦North,East,South,West¦
| argument | Remove Existing Space Shading Surfaces From the Model? | remove_ext_space_shading | static | Bool | FALSE
| argument | Optionally Choose a Construction for the Overhangs. | construction | static | Choice
FALSE | Add Simple PV to Shading Surfaces By Type | AddSimplePvToShadingSurfacesByType | EnergyPlusMeasure
| argument | Choose the Type of Shading Surfaces to add PV to | shading_type | static | Choice | Building Shading | ¦Site Shading,Building Shading,Space/Zone Shading¦
| argument | Fraction of Included Surface Area with PV | fraction_surfacearea_with_pv | static | Double | 0.5
| argument | Fractional Value for Cell Efficiency | value_for_cell_efficiency | static | Double | 0.12
| argument | Material and Installation Costs for the PV ($). | material_cost | static | Double | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the PV ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Adjust Thermostat Setpoints by Degrees | AdjustTheromstatSetpointsByDegrees | RubyMeasure
| argument | Degrees Fahrenheit to Adjust Cooling Setpoint By. | cooling_adjustment | static | Double | 1
| argument | Degrees Fahrenheit to Adjust heating Setpoint By. | heating_adjustment | static | Double | -1
| argument | Alter Design Day Thermostats? | alter_design_days | static | Bool | FALSE
FALSE | Bar Aspect Ratio Study | BarAspectRatioStudy | RubyMeasure
| argument | Total Building Floor Area (ft^2). | total_bldg_area_ip | static | Double | 10000
| argument | Ratio of North/South Facade Length Relative to East/West Facade Length. | ns_to_ew_ratio | static | Double | 2
| argument | Number of Floors. | num_floors | static | Integer | 2
| argument | Floor to Floor Height (ft). | floor_to_floor_height_ip | static | Double | 10
| argument | Surface Matching? | surface_matching | static | Bool | TRUE
| argument | Make Thermal Zones from Spaces? | make_zones | static | Bool | TRUE
FALSE | Enable Demand Controlled Ventilation | EnableDemandControlledVentilation | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Remove Baseline Costs From Effected AirLoopHVACOutdoorAirSystems? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Air Loop to Enable Demand Controlled Ventilation ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Air Loop to Enable Demand Controlled Ventilation ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Air Loop for Demand Controlled Ventilation ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Enable Economizer Control | EnableEconomizerControl | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Economizer Control Type. | economizer_type | static | Choice
| argument | Economizer Maximum Limit Dry-Bulb Temperature (F). | econoMaxDryBulbTemp | static | Double | 69
| argument | Economizer Maximum Enthalpy (Btu/lb). | econoMaxEnthalpy | static | Double | 28
| argument | Economizer Maximum Limit Dewpoint Temperature (F). | econoMaxDewpointTemp | static | Double | 55
| argument | Economizer Minimum Limit Dry-Bulb Temperature (F). | econoMinDryBulbTemp | static | Double | -148
| argument | Remove Baseline Costs From Effected AirLoopHVACOutdoorAirSystems? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Air Loop to Enable Economizer ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Air Loop to Enable Economizer ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Air Loop for Economizer ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Export Schedule CSV | ExportScheduleCSV | ReportingMeasure
| argument | Time Interval (minutes) | interval | static | Integer | 60
FALSE | Find and Replace Object Names in the Model | FindAndReplaceObjectNames | RubyMeasure
| argument | Type the text you want search for in object names | orig_string | static | String | replace this text
| argument | Type the text you want to add in place of the found text | new_string | static | String | with this text
FALSE | Improve Fan Belt Efficiency | ImproveFanBeltEfficiency | RubyMeasure
| argument | Choose an Air Loop to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Motor Efficiency Improvement Due to Fan Belt Improvements(%). | motor_eff | static | Double | 3
| argument | Remove Baseline Costs From Effected Fans? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Motor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Motor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Motor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Improve Motor Efficiency | ImproveMotorEfficiency | RubyMeasure
| argument | Choose a Plant or Air Loop to Alter. | object | static | Choice | *All Plant and Air Loops* | ¦*All Plant and Air Loops*¦
| argument | Set Motor Efficiency(%). | motor_eff | static | Double | 96
| argument | Remove Baseline Costs From Effected Fans and Pumps? | remove_costs | static | Bool | FALSE
| argument | Material and Installation Costs per Motor ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Motor ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Motor ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set R-value of Insulation for Exterior Walls to a Specific Value | IncreaseInsulationRValueForExteriorWalls | RubyMeasure
| argument | Insulation R-value (ft^2*h*R/Btu). | r_value | static | Double | 13
| argument | Increase in Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_increase_ip | static | Double | 0
| argument | One Time Retrofit Cost to Add Insulation to Construction ($/ft^2). | one_time_retrofit_cost_ip | static | Double | 0
| argument | Year to Incur One Time Retrofit Cost (whole years). | years_until_retrofit_cost | static | Integer | 0
FALSE | Set R-value of Insulation for Roofs to a Specific Value | IncreaseInsulationRValueForRoofs | RubyMeasure
| argument | Insulation R-value (ft^2*h*R/Btu). | r_value | static | Double | 30
| argument | Increase in Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_increase_ip | static | Double | 0
| argument | One Time Retrofit Cost to Add Insulation to Construction ($/ft^2). | one_time_retrofit_cost_ip | static | Double | 0
| argument | Year to Incur One Time Retrofit Cost (whole years). | years_until_retrofit_cost | static | Integer | 0
FALSE | Inject OSM Geometry into an External IDF | InjectOsmGeometryIntoAnExternalIdf | EnergyPlusMeasure
| argument | Path to Source IDF File to Use. | source_idf_path | static | String
| argument | Merge Geometry From OpenStudio Model into Source IDF File? | merge_geometry_from_osm | static | Bool | TRUE
FALSE | Predicted Mean Vote | PredictedMeanVote | RubyMeasure
| argument | Enable ASHRAE 55 Comfort Warnings? | comfortWarnings | static | Bool | FALSE
| argument | Mean Radiant Temperature Calculation Type. | meanRadiantCalcType | static | Choice | ZoneAveraged | ¦ZoneAveraged,SurfaceWeighted¦
| argument | Choose a Work Efficiency Schedule. | workEfficiencySchedule | static | Choice
| argument | Choose a Clothing Insulation Schedule. | clothingSchedule | static | Choice | clothing_schedule_display_names[0] | ¦clothing_schedule_display_names[0]¦
| argument | Choose an Air Velocity Schedule. | airVelocitySchedule | static | Choice | airVelocity_schedule_display_names[0] | ¦airVelocity_schedule_display_names[0]¦
FALSE | Reduce Electric Equipment Loads by Percentage | ReduceElectricEquipmentLoadsByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Electric Equipment Power Reduction (%). | elecequip_power_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Cost for Electric Equipment per Floor Area (%). | material_and_installation_cost | static | Double | 0
| argument | Increase in Demolition Costs for Electric Equipment per Floor Area (%). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 15
| argument | Increase O & M Costs for Electric Equipment per Floor Area (%). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Lighting Loads by Percentage | ReduceLightingLoadsByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Lighting Power Reduction (%). | lighting_power_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Cost for Lighting per Floor Area (%). | material_and_installation_cost | static | Double | 0
| argument | Increase in Demolition Costs for Lighting per Floor Area (%). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 15
| argument | Increase O & M Costs for Lighting per Floor Area (%). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Night Time Electric Equipment Loads | ReduceNightTimeElectricEquipmentLoads | RubyMeasure
| argument | Pick an Electric Equipment Definition(schedules using this will be altered) | elec_load_def | static | Choice
| argument | Fractional Value for Night Time Load. | fraction_value | static | Double | 0.1
| argument | Apply Schedule Changes to Weekday and Default Profiles? | apply_weekday | static | Bool | TRUE
| argument | Weekday/Default Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_weekday | static | Double | 18
| argument | Weekday/Default Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_weekday | static | Double | 9
| argument | Apply Schedule Changes to Saturdays? | apply_saturday | static | Bool | TRUE
| argument | Saturday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_saturday | static | Double | 18
| argument | Saturday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_saturday | static | Double | 9
| argument | Apply Schedule Changes to Sundays? | apply_sunday | static | Bool | TRUE
| argument | Sunday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_sunday | static | Double | 18
| argument | Sunday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_sunday | static | Double | 9
| argument | Material and Installation Costs per Electric Equipment Quantity ($). | material_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs Costs per Electric Equipment Quantity ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Night Time Lighting Loads | ReduceNightTimeLightingLoads | RubyMeasure
| argument | Pick a Lighting Definition From the Model (schedules using this will be altered) | lights_def | static | Choice
| argument | Fractional Value for Night Time Load | fraction_value | static | Double | 0.1
| argument | Apply Schedule Changes to Weekday and Default Profiles? | apply_weekday | static | Bool | TRUE
| argument | Weekday/Default Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_weekday | static | Double | 18
| argument | Weekday/Default Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_weekday | static | Double | 9
| argument | Apply schedule changes to Saturdays? | apply_saturday | static | Bool | TRUE
| argument | Saturday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_saturday | static | Double | 18
| argument | Saturday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_saturday | static | Double | 9
| argument | Apply Schedule Changes to Sundays? | apply_sunday | static | Bool | TRUE
| argument | Sunday Time to Start Night Time Fraction(24hr, use decimal for sub hour). | start_sunday | static | Double | 18
| argument | Sunday Time to End Night Time Fraction(24hr, use decimal for sub hour). | end_sunday | static | Double | 9
| argument | Material and Installation Costs per Light Quantity ($). | material_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs Costs per Light Quantity ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | ReduceSpaceInfiltrationByPercentage | ReduceSpaceInfiltrationByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Space Infiltration Power Reduction (%). | space_infiltration_reduction_percent | static | Double | 30
| argument | Increase in Material and Installation Costs for Building per Affected Floor Area ($/ft^2). | material_and_installation_cost | static | Double | 0
| argument | O & M Costs for Construction per Affected Floor Area ($/ft^2). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Reduce Ventilation By Percentage | ReduceVentilationByPercentage | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model. | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Design Specification Outdoor Air Reduction (%). | design_spec_outdoor_air_reduction_percent | static | Double | 30
FALSE | RemoveUnusedDefaultProfiles | RemoveUnusedDefaultProfiles | RubyMeasure
FALSE | Rename Space Surfaces Based on Parent Space and Orientation | RenameSpaceSurfacesBasedonParentSpaceandOrientation | RubyMeasure
FALSE | Replace Exterior Window Constructions with a Different Construction from the Model | ReplaceExteriorWindowConstruction | RubyMeasure
| argument | Pick a Window Construction From the Model to Replace Existing Window Constructions. | construction | static | Choice
| argument | Change Fixed Windows? | change_fixed_windows | static | Bool | TRUE
| argument | Change Operable Windows? | change_operable_windows | static | Bool | TRUE
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs for Construction per Area Used ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Rotate Building Relative to Current Orientation | RotateBuilding | RubyMeasure
| argument | Number of Degrees to Rotate Building (positive value is clockwise). | relative_building_rotation | static | Double | 90
FALSE | Set COP for Two Speed DX Cooling Units | SetCOPforTwoSpeedDXCoolingUnits | RubyMeasure
| argument | Choose an Air Loop with a two speed DX Cooling Unit to Alter. | object | static | Choice | *All Air Loops* | ¦*All Air Loops*¦
| argument | Rated High Speed COP | cop_high | static | Double | 4
| argument | Rated Low Speed COP | cop_low | static | Double | 4
| argument | Remove Baseline Costs From Effected Cooling Coil DX Two Speed Units? | remove_costs | static | Bool | TRUE
| argument | Material and Installation Costs per Cooling Coil DX Two Speed Unit ($). | material_cost | static | Double | 0
| argument | Demolition Costs per Cooling Coil DX Two Speed Unit ($). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs per Cooling Coil DX Two Speed Unit ($). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set EnergyPlus Light objects LPD | SetEnergyPlusLightObjectsLPD | EnergyPlusMeasure
| argument | Lighting Power Density (W/m^2) | lpd | static | Double | 10.76
FALSE | Set Ext Wall To Ground Boundary Condition By Story | SetExtWallToGroundBoundaryConditionByStory | RubyMeasure
| argument | Choose a Story to Change Wall Boundary Conditions For. | storyBasement | static | Choice
FALSE | Set Interior Walls to Adiabatic | SetInteriorWallsAndFloorsToAdiabatic | RubyMeasure
| argument | Select New Construction. | construction | static | Choice
FALSE | Set Interior Walls to Selected Construction | SetInteriorWallsToSelectedConstruction | RubyMeasure
| argument | Select new material: | construction | static | Choice
FALSE | Set Lifecycle Cost Parameters | SetLifecycleCostParameters | RubyMeasure
| argument | Set the Length of the Study Period (years). | study_period | static | Integer | 25
FALSE | Set Lighting Loads by LPD | SetLightingLoadsByLPD | RubyMeasure
| argument | Apply the Measure to a Specific Space Type or to the Entire Model | space_type | static | Choice | *Entire Building* | ¦*Entire Building*¦
| argument | Lighting Power Density (W/ft^2) | lpd | static | Double | 1
| argument | Material and Installation Costs for Lights per Floor Area ($/ft^2). | material_cost | static | Double | 0
| argument | Demolition Costs for Lights per Floor Area ($/ft^2). | demolition_cost | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for Lights per Floor Area ($/ft^2). | om_cost | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Space Infiltration by Exterior Surface Area | SetSpaceInfiltrationByExteriorSurfaceArea | RubyMeasure
| argument | Space Infiltration Flow per Exterior Envelope Surface Area (cfm/ft^2).) #(ft^3/min)/(ft^2) = (ft/min | infiltration_ip | static | Double | 0.05
| argument | Increase in Material and Installation Costs for Building per Exterior Envelope Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | O & M Costs for Construction per Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Window to Wall Ratio by Facade | SetWindowToWallRatioByFacade | RubyMeasure
| argument | Window to Wall Ratio (fraction). | wwr | static | Double | 0.4
| argument | Sill Height (in). | sillHeight | static | Double | 30
| argument | Cardinal Direction. | facade | static | Choice | South | ¦North,East,South,West¦
FALSE | Shift Schedule Profile Time | ShiftScheduleProfileTime | RubyMeasure
| argument | Choose a Schedule to Shift the Time For. | schedule | static | Choice | *All Ruleset Schedules* | ¦*All Ruleset Schedules*¦
| argument | Shift Schedule Profiles Forward (24hr, use decimal for sub hour). | shift_value | static | Double | 1
FALSE | Swap Lights Definition | SwapLightsDefinition | RubyMeasure
| argument | Choose the Lights Definition you Want to Replace. | old_lights_def | static | Choice
| argument | Choose the Lights Definition to Use in Place of Removed Definition. | new_lights_def | static | Choice
| argument | Demolition Costs Occur During Initial Definition? | demo_cost_initial_const | static | Bool | FALSE
FALSE | Xcel EDA Reporting and QAQC | XcelEDAReportingandQAQC | ReportingMeasure
FALSE | Xcel EDA Tariff Selection and Model Setup | XcelEDATariffSelectionandModelSetup | EnergyPlusMeasure
| argument | Select an Electricity Tariff. | elec_tar | static | Choice | Secondary General | ¦Residential General,Commercial,Primary General,Secondary General Low Load Factor,Secondary General,Secondary Photovoltaic Time-of-Use,Transmission General,Non-Xcel Commercial,Non-Xcel Primary General,Non-Xcel Secondary General Low Load Factor,Non-Xcel Secondary General,Non-Xcel Transmission General¦
| argument | Select a Gas Tariff. | gas_tar | static | Choice | Large CG | ¦Residential Gas,Small CG,Large CG,Interruptible Industrial G,Non-Xcel Gas Firm,Non-Xcel Gas Interruptible¦
FALSE | Set Boiler Thermal Efficiency | SetBoilerThermalEfficiency | RubyMeasure
| argument | Apply the measure to | boiler_widget | static | Choice | boiler_display_names[0] | ¦0,boiler_display_names[0]¦
| argument | Option 1, set boiler nominal thermal efficiency to a user defined value | input_option_manual | static | Bool | FALSE
| argument | Boiler nominal thermal efficiency (between 0 and 1) | boiler_thermal_efficiency | static | Double | 0.8
| argument | Option 2, set boiler nominal thermal efficiency based on ASHRAE Standard 90.1 requirement | input_option_standard | static | Bool | FALSE
| argument | Boiler nominal capacity [W] | nominal_capacity | static | Double
| argument | Fuel type | fuel_type_widget | static | Choice | fuel_type_display_names[0] | ¦0,1,2,fuel_type_display_names[0]¦
| argument | ASHRAE Standards 90.1 | standards_widget | static | Choice | standards_display_names[0] | ¦0,1,2,3,4,standards_display_names[0]¦
FALSE | Set Water Heater Efficiency, Heat Loss, and Peak Water Flow Rate | SetWaterHeaterEfficiencyHeatLossandPeakWaterFlowRate | RubyMeasure
| argument | Apply the measure to | waterheater_widget | static | Choice | waterheater_display_names[0] | ¦0,waterheater_display_names[0]¦
| argument | Fuel type | heater_fuel_type_widget | static | Choice | heater_fuel_type_display_names[0] | ¦heater_fuel_type_display_names[0]¦
| argument | Thermal efficiency [between 0 and 1] | heater_thermal_efficiency | static | Double | 0.8
| argument | Loss coefficient to ambient temperature [W/K] (optional input, baseline value will be used if empty) | onoff_cycle_loss_coefficient_to_ambient_temperature | static | Double | 0
| argument | Peak water use flow rate [m3/s] (optional input, baseline value will be used if empty) | peak_use_flow_rate | static | Double
FALSE | SetChillerCOP | SetChillerCOP | RubyMeasure
| argument | Apply the measure to | chiller_widget | static | Choice | *All chillers* | ¦*All chillers*¦
| argument | Chiller Rated COP (more than 0) | chiller_thermal_efficiency | static | Double | 3 |  | 2.5 | 5.5 | 4 | 0.5 | triangle_uncertain
FALSE | Set Minimum VAV Terminal Flow Fraction | SetMinimumVAVTerminalFlowFraction | RubyMeasure
| argument | Minimum VAV Terminal Flow Fraction (%) | min_vav_frac | static | Double | 30
FALSE | Add Cost per Floor Area to Building | AddCostPerFloorAreaToBuilding | RubyMeasure
| argument | Remove Existing Costs? | remove_costs | static | Bool | TRUE
| argument | Name for Life Cycle Cost Object. | lcc_name | static | String | Building - Life Cycle Costs
| argument | Material and Installation Costs for the Building per Floor Area ($/ft^2). | material_cost_ip | static | Double | 0
| argument | Demolition Costs for Construction per Area Used ($/ft^2). | demolition_cost_ip | static | Double | 0
| argument | Years Until Costs Start (whole years). | years_until_costs_start | static | Integer | 0
| argument | Demolition Costs Occur During Initial Construction? | demo_cost_initial_const | static | Bool | FALSE
| argument | Expected Life (whole years). | expected_life | static | Integer | 20
| argument | O & M Costs for the Builiding per Floor Area Used ($/ft^2). | om_cost_ip | static | Double | 0
| argument | O & M Frequency (whole years). | om_frequency | static | Integer | 1
FALSE | Set Heating and Cooling Sizing Factors | SetHeatingandCoolingSizingFactors | RubyMeasure
| argument | Heating Sizing Factor (eg 1.25 = 125% of required heating capacity. | htg_sz_factor | static | Double | 1.25
| argument | Coolinig Sizing Factor (eg 1.15 = 115% of required cooling capacity. | clg_sz_factor | static | Double | 1.15
FALSE | SetChillerCOP | SetChillerCOP | RubyMeasure
| argument | Apply the measure to | chiller_widget | static | Choice | *All chillers* | ¦*All chillers*¦
| variable | Chiller Rated COP (more than 0) | chiller_thermal_efficiency | lhs | Double | 3 |  | 2.5 | 5.5 | 4 | 0.5 | triangle_uncertain
FALSE | Set Chilled Water Loop Temperature | SetChilledWaterLoopTemperature | RubyMeasure
| argument | Desired chilled water setpoint (F) | cw_temp_f | static | Double | 45
FALSE | Set Hot Water Loop Temperature | SetHotWaterLoopTemperature | RubyMeasure
| argument | Desired hot water setpoint (F) | hw_temp_f | static | Double | 140

## Lookups
Instances | Number of Cores | Cost
m3.large | 2 Cores | $0.14/hour | - Recommended for Server
m3.xlarge | 4 Cores | $0.28/hour | - Recommended for Server
m3.2xlarge | 8 Cores | $0.56/hour | - Recommended for Server
c3.large | 2 Cores | $0.11/hour | - Worker Only -
c3.xlarge | 4 Cores | $0.21/hour | - Worker Only -
c3.2xlarge | 8 Cores | $0.42/hour | - Worker Only - Recommended for Worker
c3.4xlarge | 8 Cores | $0.84/hour | - Worker Only - Recommended for Worker
c3.8xlarge | 16 Cores | $1.68/hour | - Worker Only - Recommended for Worker
SensitivityType |  | TrueFalse |  | Workflow |  | Simulation
individual_variables |  | TRUE |  | run_openstudio_workflow.rb |  | simulate_data_point.rb
all_variables |  | FALSE |  | run_openstudio_workflow_monthly.rb
AnalysisType |  | batch_run |  |  | lhs |  |  | Optim |  |  | Rgenoud |  |  | Nsga |  |  | preflight | sequential_search
batch_run |  |  |  |  | Sample Method | individual_variables | individual_variables / all_variables | epsilonGradient | 0.01 | epsilon in gradient calculation | popSize | 30 | Size of initial population | Number of Samples | 30 | Size of initial population
lhs |  |  |  |  | Number of Samples | 30 | positive integer (if individual, total simulations is this times each variable) | pgtol | 0.01 | tolerance on the projected gradient | Generations | 5 | Number of generations | Generations | 3 | Number of generations
optim | [7 empty] | factr | 45036000000000 | Tolerance on delta_F | waitGenerations | 2 | If no improvement in waitGenerations of generations, then exit | cprob | 0.85 | Crossover probability [0,1]
rgenoud | [7 empty] | maxit | 100 | Maximum number of iterations | bfgsburnin | 2 | The number of generations which are run before the BFGS is ﬁrst used | XoverDistIdx | 2 | Crossover Distribution Index (large values give higher probabilities of offspring close to parent)
nsga_nrel | [7 empty] | normType | minkowski |  | solutionTolerance | 0.01 | Numbers within solutionTolerance are considered equal | MuDistIdx | 2 | Mutation Distribution Index (large values give higher probabilities of offspring close to parent)
preflight | [7 empty] | pPower | 2 | Lp norm power | epsilonGradient | 0.01 | epsilon in gradient calculation | mprob | 0.8 | Mutation probability [0,1]
sequential_search | [10 empty] | pgtol | 0.01 | tolerance on the projected gradient | normType | minkowski
singlerun | [10 empty] | factr | 45036000000000 | Tolerance on delta_F | pPower | 2 | Lp norm power
[11 empty] | maxit | 100 | Maximum number of iterations
[11 empty] | normType | minkowski
[11 empty] | pPower | 2 | Lp norm power